QSFP+-40G-SR4

40Gb/s QSFP+ SR4 Transceiver Module

### Feature

- RoHS-6 compliant

- High speed / high density: support up to

4X10 Gb/s bi-directional operation

- Compliant to industrial standard SFF-8436 QSFP+ standard

- Low power consumption : less than 1.5W

- Distance up to 100 meters by OM3 fiber and 150M

by OM4 fibe

- Reliable VCSEL and PIN photonic devices

- I2C standard management interface

- Excellent high speed signal integrity

### Description

The WTQSFP+-SR4 is a 40Gbps, hot pluggable fiber transceivers for Infiniband QDR and 40G Ethernet data transmission. It provides full duplex, parallel interconnects: 4 transmitting / 4 receiving data lanes and each lane at data rate up to 10.3125Gbps.

Distance support could be up to 100 meters using OM3 fiber and 150 meters using OM4 fiber. Each lane could also be configured as independent 10G Ethernet transmission. Therefore facilitate higher port density at 10G Ethernet.

WTQSFP+-SR4 is designed to meet the requirements of high speed, high density and low power consumption for applications in today’s data centers.

### Application

-  40G Ethernet (40GBASE-SR4)

-  Proprietary high speed, high density data transmission.

-  Switch and router high speed backplane interconnect

-  High performance computing, server and data storage.

### Absolute Maximum Ratings

| Parameter | Symbol | Min | Typ | Max | Units | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| Storage Temperature | TS | -40 |  | 85 | °C |  |
| Storage Ambient Humidity | HA | 0 |  | 85 | % |  |
| +3.3V Power Supply | VCC3 | 0 |  | 3.6 | V |  |

### General Operating Characteristics

| Parameter | Symbol | Min | Typ | Max | Units | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| Operating Case Temperature | TC | 0 |  | 70 | °C | [1] |
| Ambient Humidity | HA | 5 |  | 85 | % | [2] |
| +3.3V Supply Voltage | VCC3 | 3.135 |  | 3.465 | V |  |
| +3.3V Supply Current | IVCC3 |  |  | 400 | mA |  |
| Total Power Dissipation | PD |  |  | 1.5 | W |  |
| Bit rate | B |  | 10.3125 |  | Gb/s | [3] |
| Input Control Voltage- High | ViH | 2.0 |  | Vcc+0.3 | V | [4] |
| Input Control Voltage - Low | ViL | -0.3 |  | 0.8 | V | [4] |
| Digital Output Voltage- High | VoH | 2.0 |  | Vcc+0.3 |  | [5] |
| Digital Output Voltage- Low | VoL | 0 |  | 0.8 |  | [5] |
| Clock Rate-I2C |  |  |  | 400 | kHz | [6] |

Notes:

1. See ordering information. The position for measuring case temperature is shown as following

2. Non-condensing

3. Tested with PRBS 231-1, BER 1X10-12

4. For all control input pins: LPMode, Reset and ModSelL

5. For all status output pins: ModPrsL , IntL

6. For management interface.

### High Speed Characteristics- Transmitter

| Parameter | Symbol | Min | Typ | Max | Units | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| Reference Differential Input Impedance | Zd |  | 100 |  | Ω |  |
| Central Wavelength |  | 840 |  | 860 | nm |  |
| Spectral Width | σ |  |  | 0.65 | nm |  |
| Differential Data Input Swing | Vin_pp | 180 |  | 600 | mV |  |
| Differential Data Input Threshold |  |  | 50 |  | mV | [1] |
| Average Launch Power | Po | -7.6 |  | 2.4 | dBm | Each lane |
| Peak Average Launch Power |  |  |  | 4 | dBm |  |
| Average Launch Power at OFF |  |  |  | -30 | dBm | Each lane |
| Optical Modulation Amplitude | OMA | -5.6 |  | 3 | dBm | Each lane |
| OMA difference |  |  |  | 4 | dB | Any2lanes |
| Transmitter Dispersion Penalty | TDP |  |  | 3.5 | dB | Each lane |
| Extinction Ratio | ER | 3 |  |  | dB |  |
| Optical Return Loss Tolerance | ORL |  |  | 12 | dB |  |
| Encircled Flux | ≧86% in 38um diameter ≦30% in 9um diameter |  |
| Eye Mask | Meet IEEE802.3BA Tab 86-6 | [2] |

Notes:

1. Input swing to trigger TX-squelch.

2. Hit ratio: 5X10-5

### High Speed Characteristics- Receiver

| Parameter | Symbol | Min | Typ | Max | Units | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| Reference Differential Input Impedance | Zd |  | 100 |  | Ω |  |
| Differential Output Swing |  | 400 |  | 800 | mV | [1] |
| Differential Output Swing When Squelched |  |  |  | 50 | mV |  |
| Rise / Fall Time (20% ~80%) |  | 24 |  |  | ps |  |
| Central Wavelength |  | 840 |  | 860 | nm |  |
| Average Power at Receiver Input |  | -9.5 |  | +2.4 | dBm | Each lane [2] |
| Damage Threshold | DT |  |  | 3.4 | dBm | Each lane [2] |
| LOS De-Assert |  |  |  | -9.5 |  |  |
| LOS Assert |  | -27 |  |  |  |  |
| LOS Hysteresis |  | 0.5 |  |  |  |  |

Notes:

1. Receiver output swing could be changed by I2C interface.

2. Measured with reference optical input with PRBS2^31-1 BER:1E-12 at ER:4.75 dB

### 8. Pin Description

QSFP Module Pad Layout (Top View)

Host PCB Layout (Top View)

- Module Electrical Pin Function Definition

| Pin | Logic | Symbol | Name/Description | Note |
| --- | --- | --- | --- | --- |
| 1 |  | GND | Ground | [1] |
| 2 | CML-I | Tx2n | Transmitter Inverted Data Input |  |
| 3 | CML-I | Tx2p | Transmitter Non-inverted Data Input |  |
| 4 |  | GND | Ground | [1] |
| 5 | CML-I | Tx4n | Transmitter Inverted Data Input |  |
| 6 | CML-I | Tx4p | Transmitter Non-inverted Data Input |  |
| 7 |  | GND | Ground | [1] |
| 8 | LVTTL-I | ModSelL | Module Select |  |
| 9 | LVTTL-I | ResetL | Module Reset |  |
| 10 |  | Vcc Rx | +3.3V Power Supply Receiver |  |
| 11 | LVCMOS-I/O | SCL | 2-Wire Serial Interface Clock | [2] |
| 12 | LVCMOS-I/O | SDA | 2-Wire Serial Interface Data | [2] |
| 13 |  | GND | Ground | [1] |
| 14 | CML-O | Rx3p | Receiver Non-Inverted Data Output |  |
| 15 | CML-O | Rx3n | Receiver Inverted Data Output |  |
| 16 |  | GND | Ground | [1] |
| 17 | CML-O | Rx1p | Receiver Non-Inverted Data Output |  |
| 18 | CML-O | Rx1n | Receiver Inverted Data Output |  |
| 19 |  | GND | Ground | [1] |
| 20 |  | GND | Ground | [1] |
| 21 | CML-O | Rx2n | Receiver Inverted Data Output |  |
| 22 | CML-O | Rx2p | Receiver Non-Inverted Data Output |  |
| 23 |  | GND | Ground | [1] |
| 24 | CML-O | Rx4n | Receiver Inverted Data Output |  |
| 25 | CML-O | Rx4p | Receiver Non-Inverted Data Output |  |
| 26 |  | GND | Ground | [1] |
| 27 | LVTTL-O | ModPrsL | Module Present | [2] |
| 28 | LVTTL-O | IntL | Interrupt | [2] |
| 29 |  | Vcc Tx | +3.3V Power Supply Transmitter |  |
| 30 |  | Vcc1 | +3.3V Power Supply |  |
| 31 | LVTTL-I | LPMode | Low Power Mode |  |
| 32 |  | GND | Ground | [1] |
| 33 | CML-I | Tx3p | Transmitter Non-inverted Data Input |  |
| 34 | CML-I | Tx3n | Transmitter Inverted Data Input |  |
| 35 |  | GND | Ground | [1] |
| 36 | CML-I | Tx1p | Transmitter Non-inverted Data Input |  |
| 37 | CML-I | Tx1n | Transmitter Inverted Data Input |  |
| 38 |  | GND | Ground | [1] |

Notes:

1. Module ground pins GND are isolated from the module case and chassis ground within the module.

2. Shall be pulled up with 4.7K-10Kohms to a voltage between 3.15V and 3.45V on the host board.

### Mechanical Specification

### 10. Regulatory Compliance

| Feature | Test Method | Reference |
| --- | --- | --- |
| Electrostatic Discharge (ESD) to the Electrical Pins | Human Body Model (HBM) | MIL-STD-883E Method 3015.7 EIA-JESD22-A114 |
|  | Machine Model (MM) | EIA-JESD22-A115 |
| Electrostatic Discharge (ESD) to the Simplex Receptacle | Contact Discharge | IEC/EN 61000-4-2 |
|  | Air Discharge | IEC/EN 61000-4-2 |
| Electromagnetic Interference (EMI) |  | FCC Part 15 Class B EN 55022 Class B (CISPR 22A) |
| Laser Eye Safety | FDA/CDRH TUV | FDA 21CFR 1040.10, 1040.11 EN 60825-1 EN 60825-2 |